## Slide 1
PIPEWORK SUPPORT SYSTEMS

## Slide 2
Pipe supports are an important part of any piping system and are considered to be an integral part of the piping design.
It is true to say that the piping system will only be good as what is holding it in place.

## Slide 33
By the consideration of pipe routes at an early stage, structural members and plant items can be arranged in the most convenient positions to give a simple and economical and safe arrangement for supporting the pipework.
Piping Supports

## Slide 34
Pipe Rack Structure and Equipment Components

## Slide 36
Main factors to consider when installing pipe support systems
To allow or control expansion and contraction of
pipes as they heat up and cool down.
To absorb or minimise vibration transmitted to pipes
from operating equipment.
To counteract pipe movement or shock caused by
rapid changes in flow through pipes.

## Slide 37
Piping Supports
Piping must be supported in such a way as to prevent its weight from being carried by the equipment to which it is attached.
The supports used must prevent excessive sagging of the pipe and at the same time must allow free movement of the pipe due to expansion or contraction.

## Slide 38
The supporting arrangement must be of minimum design to carry the weight of the pipe, valves, fittings and insulation plus the weight of the fluid contained within the pipe.
Basically, the heaviest load that the system may possibly have to carry.
Piping Supports

## Slide 39
Supports are available in many different designs, but they are usually divided into two categories:
pipe supports, which support pipes from underneath.
(2) pipe hangers, which secure pipes from above.
The choice of which is used depends on the requirements of the particular system.
Piping Supports

## Slide 40
Hangers
Hangers consist of a pipe clip round the pipe, a sling rod and a top attachment to the supporting steelwork.
1 Upper component - fixed attachment
2 Intermediate component - adjustable section
3 Lower component - pipe clip

## Slide 41
Upper component - fixed attachment
Intermediate component - adjustable section
Lower component - pipe clip/strap

## Slide 42
Support design

## Slide 43
UPPER COMPONENTS - FIXTURE
Clamps and fittings designed to specification

## Slide 44
UPPER COMPONENTS- FIXTURE
Welded brackets to underside of beam
Beam clamp

## Slide 45
INTERMEDIATE COMPONENTS - ADJUSTABLE
Drop-rod
Turnbuckle

## Slide 47
Constant load spring hanger
INTERMEDIATE COMPONENTS - ADJUSTABLE

## Slide 48
Constant hangers and constant supports are used for piping and related components where higher levels of vertical travel occur.
Their job is to transfer the working load over the whole travel area while maintaining constancy, i.e., without any considerable deviations.

## Slide 49
INTERMEDIATE COMPONENTS - ADJUSTABLE
Variable load spring hanger

## Slide 51
Variable support hangers are also used to support pipes, that experience vertical movement.
Unlike constant support hangers, the variable support hangers are used where the supporting components have the capability to withstand load variations of up to 25%.
Variable load spring hanger

## Slide 52
LOWER COMPONENTS - HOLDING

## Slide 53
LOWER COMPONENTS - HOLDING

## Slide 56
Supporting pipework from beneath

## Slide 58
Pipe Skids

## Slide 59
Pipe Skids

## Slide 60
SUPPORTS – HOLD FROM BENEATH
Welded elbow support
Saddle support

## Slide 63
Variable load spring support

## Slide 64
Adjustable to suit compressive pipe loading

## Slide 65
Constant load spring support

## Slide 66
Support rollers and chairs

## Slide 67
U-bolts
U-bolt, horizontal fix or guide
U-bolt, vertical fix or guide

## Slide 68
SUPPORT FRAME

## Slide 69
CANTILEVERS

## Slide 71
Pipe racks and bridges

## Slide 73
Pipe rack support frames

## Slide 76
Supports should be of ample strength to carry the most severe load combination:-
Weight of pipe, fittings, valves etc.
Weight of operating or test fluid
whichever the greater.

## Slide 77
Weight of insulation.(wet)
Weight of pipe support components.
Expansion and contraction loads.
Reaction from line discharging to atmosphere.
Wind, snow and ice loads.
Any other forces. (people climbing)

## Slide 78
Consideration should also be given to:
Any forces arising from two-phase flow.
Need to control the magnitude of forces and
moments on equipment.
Vibrations.
Settlement of large storage tanks.
Removal of pipework or equipment for maintenance.
Access to equipment.
Differential settlement of the building.

## Slide 79
Avoiding damage to any pipe insulation.
Avoiding stress concentration at the point of attachments to the pipe
Process mal-operation or just plainly the unexpected, e.g. Gas lines filling up with water or dust/silt.
Expansion joints in the building structure.
The effect of ‘Water’ hammer.

## Slide 80
POSITIONING OF PIPE
The position of the pipe will determine type of support to be used.
Pipe routing usually has to be made with the supports required in mind.

## Slide 82
Pipes should be grouped to minimise the
number of structural members needed solely
for the supporting of pipes.
Supports should be located to reduce the
necessity for temporary supports.
Where regular maintenance requires removal
of equipment, vessel covers, control valves etc.
Where the pipes must be dismantled for cleaning.
POSITIONING OF PIPE

## Slide 83
Where practical, a support should be located immediately adjacent to any change in direction of the pipes.
Supports should not be located on sharp radius bends or weld elbows which are already subjected to high localised stresses but should be located at points of low stress in pipes.
POSITIONING OF PIPE

## Slide 84
Screwed or flanged joints should not be sited at mid span or close to a support (i.e. at high points of high bending moment).
POSITIONING OF PIPE

## Slide 85
Pipes from upper connections on tall free standing vertical vessels (e.g. distillation columns) are supported from the vessel to minimise relative movement between support and the pipes.
POSITIONING OF PIPE

## Slide 87
Support Inspection
Corrosion at pipe supports is one of the leading causes of process piping failures.
It is the beam supports and saddle clamps that have historically caused the majority of problems.

## Slide 98
Design (product insufficiencies or a mistake in their application)
Installation (improper hanger position or calibration)
Fabrication (substandard manufacture/quality)
Service (cyclic loading, adverse environment or operational events)
Hanger degradation and ultimate failure, thus transferring unsupported static load back into the piping systems and increasing stress levels.
Generally, the root causes of failure with hangers and their associated piping include:

## Slide 99
Inspections Are Critical for Piping Safety
Hanger Problems
Adverse consequences arising from improper hanger performance include unpredictable stress and elevation changes within the suspended piping.
Problem areas are often the result of root causes acting independently of one another or in various combinations.

## Slide 100
Checklist for Inspection of Hanger Assembly
Check the beam attachment, pin and the spring hanger attachment for any cracks, fractures, or signs of corrosion.
Check the pipe clamp attachment, the weldless eye and threaded rod for integrity.
Test the turnbuckle, locknuts, and other threaded items to be sure they will turn.
Check the spring coil for any sign of corrosion.

## Slide 101
Corrosion
Crevices – the formation of a crevice at the pipe surface.
Water Entrapment – water is trapped and held in contact with the pipe surface.
Poor Inspect - ability and Maintainability – virtually impossible to paint or otherwise maintain; visual and/or NDT inspection are often difficult.
Galvanic Couples – even when both the pipe and support are steel, the metallurgical differences can still provide enough potential difference to drive a corrosion cell.

## Slide 103
A FLAT SURFACE
A CREVICE FORMS
CORROSION SPREADS
PIPE FAILS

## Slide 108
PIPE SUPPORT FAILURE

## Slide 116
A “Temporary rope support” !!!