LESSON PLAN

LESSON PLAN No: E-LP-017	Dept: Electrical

SUBJECT: DOMESTIC POWER INSTALLATION	Previous Knowledge: Minimal / None

AIMS:  At the end of the delivery session the apprentice will have improved knowledge and understanding of the basic
principles of domestic power installations and be able to demonstrate how to install associated cables and
equipment and how to test circuits using appropriate test instruments and methods.

Note: -	this lesson may be taught in conjunction with the Domestic Lighting Installation therefore common aspects, such as circuit protection, cable preparation and installation, and installation testing, may be combined.

| Target Time | Learning Reference | Objectives / content | Training Officer Activity | Learner Activity | Resources |  | Assessment |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Handouts | Equipment |  |
| Session 1:25 to 1:50 hrs | Domestic installations | Review of previous session Purpose of individual circuits & how they are protected Consumer Unit Safety in the home – consequence of faulty / poor installation Dangers of extension leads | Lecture & promote Q&A & interactive discussion as the session progresses Reference to IET Regulations (17th Edition) &/or On-Site Guide as required | Observation & participation in Q&A & group discussion Visual inspection of damaged equipment Reference to IET Regulations (17th Edition) as directed &/or required | IET Regulations (17th Edition) & On-Site Guide | Dry marker board & pens Workshop installations Selection of damaged equipment Consumer Unit Single switched socket outlet Twin switched socket outlet Socket patress’ Cable – flat twin-&-earth (2.5mm2) Miniature Circuit Breaker (MCB) | Observation / Q&A individuals & group during delivery & during the group assignment |
|  | Power installations | Power circuit equipment Circuit protection MCB type & rating Cables Terminology (Phase, Neutral, CPC, Final Ring, Radial) Equipment – purpose, installation & limitations Power installations - schematic & wiring diagrams for : - final-ring circuits - radial circuits Spur junctions - installation, protection & limitations |  |  |  |  |  |

LESSON PLAN

LESSON PLAN No: E-LP-017	Dept: Electrical

SUBJECT: DOMESTIC POWER INSTALLATION	Previous Knowledge: Minimal / None

| Target Time | Learning Reference | Objectives / content | Training Officer Activity | Learner Activity | Resources |  | Assessment |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Handouts | Equipment |  |
| Session 2 1.40-1.50 hrs | Inspection & testing | Visual inspection requirements Test instruments – safe handling & operation Electrical testing : - Continuity test - Insulation test Min / Max values (see E-LP-017 Addendum) | Lecture & promote Q&A & interactive discussion as the session progresses Reference to E-LP-017 (Addendum) Demonstration of testing procedure / process & how to interpret results Reference to IET Regulations (17th Edition) &/or On-Site Guide as required | Observation & participation in group discussion & feedback Reference to IET Regulations (17th Edition), On-Site Guide &/or Domestic Lighting & Power Worksheet E-AG-011 as directed &/or required | IET Regulations (17th Edition) – Part 6 Chapter 61 IET On-Site Guide – Sections 9 & 10 Domestic Lighting & Power Worksheet E-AG-011 | Hand tools (terminal screwdriver) 500/1000V Megger & test leads | Observation / Q&A individuals & group during delivery Review of Risk Assessment content |
| Session 2 (cont’d) | Health & Safety | Visual inspection of hand tools, practical assignment equipment & local work environment Preparation of equipment Workplan | Promote close inspection of equipment & identify potential hazards Demonstration : preparation of cable & termination, safe use of hand tools & equipment to complete the practical assignment | Observation & participation in group discussion & feedback | Domestic Lighting & Power Worksheet E-AG-011 | Hand tools & test instruments |  |
|  |  | Risk Assessment | Provide assistance / information / guidance on demand during the activity & inspect the completed Assessment | Group assignment - complete a Risk Assessment of proposed practical activity | Risk Assessment form HS-R-048 | Dry marker board & pens |  |

LESSON PLAN

LESSON PLAN No: E-LP-017	Dept: Electrical

SUBJECT: DOMESTIC POWER INSTALLATION	Previous Knowledge: Minimal / None

| Target Time | Learning Reference | Objectives / content | Training Officer Activity | Learner Activity | Resources |  | Assessment |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Handouts | Equipment |  |
| Sessions 3 & 4 3.40-7.5 hrs | Power installation | Using the notes in E-AG-011 & the previously completed schematic diagrams, construct Power Installation for : - Three twin socket ring Visually inspect & test each circuit using approved methods & instruments Record & interpret results | Provide information / guidance / support on demand during the assignment activity Observe & Q&A during the Inspection & Testing activity Highlight hazards prior to connection of completed circuits to the supply Connect, visually test &, when complete, remove the mains connection. | Practical assignment - Apprentices to work in teams of 2 & follow the instructions in the Worksheet (E-AG-011). Inspect & test completed circuits (to be observed by the Instructor) & results recorded in the relevant section of the Worksheet (E-AG-011) | Domestic Lighting & Power Worksheet E-AG-011 | Work board (5’x4’) Consumer Unit with 32A MCB Socket outlet (x3) Socket patress (x3) Cable – flat twin-&-earth (2.5mm2) Cable clips Hand tools Earth sleeving Test lead & RCD (instructor use ONLY) Polarity Tester | Observation of practical activity & assessment of knowledge during practical assignment Note : connection to the mains supply to assess the completed circuits may be repeated if a fault is observed / detected |
| Sessions 3 & 4 (cont’d) | Power installation | Complete a written assignment of the practical task as instructed in the Worksheet E-AG-011 | Provide information / guidance / support on demand during the assignment activity | Complete written assignment as instructed in the Worksheet E-AG-011 | Domestic Lighting & Power Worksheet E-A-008 | Practical task notes Pen, pencil, ruler, lined paper | Assessment of written content of assignment Note : content may be aligned with the Domestic Lighting assignment hence common aspects need not be repeated |

LESSON PLAN

LESSON PLAN No: E-LP-017 (ADDENDUM)	Dept: Electrical

SUBJECT: DOMESTIC POWER INSTALLATION (TEST PROCEDURE)	Previous Knowledge: Minimal / None

Prior to making the final connection to the mains (230Vac) supply:

Inspection: Circuits must be visually inspected as per the Worksheet (E-AG-011).

Continuity Testing

- At the Consumer Unit, ensure all power circuit conductors are disconnected and accessible for visual inspection and testing

- Prepare and/or calibrate the Test Instrument, select Ohms (Ω) and attach the leads together in order to assess the test-lead resistance

For a Final Ring connected circuit:

- At the Consumer Unit, select the final ring main conductors connect the test leads to the two Circuit Protective conductors (CPC) and observe the test reading (R2). Record the continuity resistance value in the Worksheet table

- Repeat the test by connecting the test leads across the remaining pairs of conductors (Phase-Phase, Neutral-Neutral) and observe / record the test reading in the Worksheet table

- At the Consumer Unit, connect the outgoing Phase conductor to the incoming Neutral and vice-versa, (R1+Rn). Measure the resistance between Phase and Neutral at each socket outlet (R1+Rn)/4 Ω (Note : resistance at a spur socket will be greater)

- At the Consumer Unit, connect the outgoing Phase conductor to the incoming CPC and vice-versa, (R1+R2). Measure the resistance between Phase and CPC at each socket outlet (R1+R2)/4 Ω (Note : resistance at a spur socket will be greater)

Insulation Testing

- Check all circuit equipment is connected and any electronic devices are removed

- Select “500V MegOhms” (MΩ) on the Test Instrument

- At the Consumer Unit attach the Test Instrument leads to any two of the lighting circuit conductors (CPC-Live, Live-Neutral, CPC-Neutral)

- Press the “Test” push-button on the Test Instrument and keep it pressed until a steady reading is obtained

- Observe and record the value of insulation resistance in the Worksheet table

- At the Consumer Unit, repeat the test across the remaining two pairs of conductors and record the insulation values accordingly

On completion of the testing process, reconnect the conductors to their relevant terminals in the Consumer Unit.

| Equality & Diversity | Differentiated Learning Activities (Highlight or tick where applicable) |
| --- | --- |
| Challenge stereotypes by: - Using non discriminatory language. - Using diverse images, names & scenarios. Promote a positive learning environment by : - Being a positive role model. - Encouraging collaborative work. - Valuing individual characteristics and experiences. - Encouraging learners to participate. - Nurturing mutual respect. - Promoting positive behaviour. Promote inclusion by : - Anticipating and addressing potential barriers to learning. - Using accessible resources. | - Was a mix of individual, paired and group work required?  - Variety of activities for different learning styles.  - Is learning support required  (If ticked record in action plan) - Targeted differentiated questioning to check learning with prompts / leads to support less able learners.  Specific Differentiation activities: - By Extension  (For example additional practical tasks after completion of ROA/QCF/TECH CERT content) - By Group Work  (For example grouping learners of mixed ability y to support each other within the peer group) - By Content.  (For example study different resource materials within the same topic area) - By Activities.  (For example study the same content but do different activities) - By Gradation  ( For example the same information and activities are given as the activity becomes progressively more difficult) |
| LESSON NOTES |  |